## SAP Q Process Explained
SAP Appendix Q – MEV Data entry process
Version 02 April 2008 |  | (*) Table Q1 & Q2 are found on the individual manufacturer's test data sheets Download these from the website database

## SAP Q MEV_Savings_Calculation
SAP Q Calculation process for MEV systems
SAP Assessment Reference
Manufacturer
Product Name
Duct type
Wet room configuration
Step 1: Data Input from SAP Appendix Q Data Sheet |  | Adjusted value
If rigid ductwork is specified enter SAP Q Specific fan power from Table Q1 (*) here | Box Q01
If flexible ductwork is specified enter SAP Q Specific fan power from Table Q2 (*) here | Box Q02
Only enter one figure in either Box Q01 or Q02
Step 2: MEV Systems annual savings (See note below)
Volume of dwelling, box (6), m³ | Box Q03
Adjusted specific fan power of MEV system, W/(l/s)
Energy saved (kWh/yr), to be entered in box (95) | 0
Additional energy consumed (kWh/yr), to be entered in box (96) | #VALUE!
The CO2 emissions from the SAP calculation now incorporate savings from the tested MEV unit
Important note If any of the SAP data input items are subsequently amended this spreadsheet must be used again to recalculate the data for boxes (95) and (96)
(*) Table Q1 & Q2 are found on the individual manufacturer's test data sheets Download these from the website database
Version 02 April 2008
Note on B18: NOTE FOR SAP Q WORK GROUP ONLY This SFP figure is the straight SAP Q figure automatically multiplied by appropriate in-use factor for rigid or flexible ductwork depending on data entry Rigid ductwork = +40% Flexible ductwork = +70%
Note on F10: Uses agreed +40% In use rating for rigid ductwork
Note on F11: Uses agreed +70% In use rating for rigid ductwork
Note on C18: Ross Holleron: Brian - Looks as if the '0' in Box B10 (Rigid) is resulting in a prediction that all fan power energy consumption is being avoided. Therefore saving of 98 kWh/yr? Can we stop this happening? BA - amendments to D10, D11 and B18