## SAPQ Process Explained
SAP Appendix Q – MVHR Data entry process
Version 02 April 2008
(*) Table Q2 & Q3 are found on the individual manufacturer's test data sheets Download these from the website database
Enter the equivalent air leakage rate produced in
BOX Q11 (Yellow)into the original SAP calculation
Enter the resulting figures from BOX Q13 and BOX Q14 (Yellow) in BOX 95 and BOX 96 of the main SAP worksheet or SAP Q section of software
Submit both Product Data sheet and completed calculation spreadsheet to Building Control with main SAP assessment
Enter the revised dwelling CO2 emission/m2 into
BOX Q12 of the calculation spreadsheet
The fuel for BOX 95 and 96 is electricity
Rigid ductwork
systems
Only use Specific Fan Power and Temperature Ratio figures from Table Q2 (*)
Identify exhaust terminal configuration from design specification
Select appropriate Specific Fan Power figure for this configuration from the GREEN column in
Table Q2 (*)
Enter this figure in
BOX Q07 of the calculation spreadsheet
Select appropriate heat exchange efficiency % for this configuration from the GREEN column in
Table Q2 (*)
If the system uses insulated ductwork enter this figure in
BOX Q09 of the calculation spreadsheet
If the system uses Uninsulated ductwork enter this figure in
BOX Q10 of the calculation spreadsheet
Flexible ductwork
systems
Only use Specific Fan Power and Temperature Ratio figures from Table Q3 (*)
Identify exhaust terminal configuration from design specification
Select appropriate Specific Fan Power figure for this configuration from the GREEN column in
Table Q3 (*)
Enter this figure in
BOX Q08 of the calculation spreadsheet
Select appropriate heat exchange efficiency % for this configuration from the GREEN column in
Table Q3 (*)
If the system uses insulated ductwork enter this figure in
BOX Q09 of the calculation spreadsheet
If the system uses Uninsulated ductwork enter this figure in
BOX Q10 of the calculation spreadsheet
Enter all data into main SAP calculator selecting MVHR as the ventilation system.
Using the design specification decide whether the MVHR system features rigid or flexible ductwork
Enter the resulting CO2 emission/m2 in BOX Q01 of
SAP Q calculation spreadsheet
Enter dwelling specific data such as floor area, volume, storey, sheltered sides and air leakage in
Boxes Q02 – Q06 of calculation spreadsheet
If the SAP calculator allows different values of SFP and heat exchange efficiency to be used, all calculations (steps 1, 4 and 5 of SAP Q spreadsheet) must be completed using the default values of 2 W/l/s and 66% efficiency.

## SAP Q MVHR_Savings_Calculation
SAP Q Calculation process for MVHR systems
SAP Assessment Reference
Manufacturer
Product Name
Duct type
Wet room configuration
Step 1 : Enter all data into SAP calculator, selecting MVHR as the ventilation system (* See note below)
Enter the resulting CO2 emission per m² here: |  | Box Q01
Step 2 : Enter data in the green cells below
Dwelling data: |  |  | #DIV/0! | Adjusted air change rate (22)
Total floor area of dwelling, box (5), m² |  | Box Q02 | #DIV/0! | minimum mechanical throughput
Volume of dwelling, box (6), m³ |  | Box Q03 | #DIV/0! | mechanical throughput
Number of chimneys, box (7) |  | Box Q03a
Number of open flues, box (8) |  | Box Q03b
Number of storeys |  | Box Q04 | hide E to H and 28, 34, 43, 44
Number of sides sheltered, box (20) |  | Box Q05
Design or measured air leakage at 50 pascals, m³/m².h |  | Box Q06
Step 3: Data Input from SAP Appendix Q Data Sheet |  |  | Adjusted value
If rigid ductwork is specified enter SAP Q Specific fan power from Table Q2 (*) here |  | Box Q07
If flexible ductwork is specified enter SAP Q Specific fan power from Table Q3 (*) here |  | Box Q08
Adjusted specific fan power of MHVR system, W/(l/s)
Only enter one figure in either Box Q07 or Q08 Rigid ductwork use Table Q2 (*), Flexible ductwork use Table Q3 (*)
If insulated ductwork is specified enter SAP Q Heat exchanger efficiency here - (From Table Q2 (*) for rigid, Table Q3 (*) for flexible) |  | Box Q09
If uninsulated ductwork is specified enter SAP Q Heat exchanger efficiency here - (From Table Q2 (*) for rigid, Table Q3 (*) for flexible) |  | Box Q10
Adjusted MVHR efficiency, % |  |  | q50* | (22) | min | n-mech
|  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Only enter one figure in either Box Q09 or Q10 Rigid ductwork use Table Q2 (*), Flexible ductwork use Table Q3 (*) |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Equivalent air leakage at 50 Pa to calculate value for box (95) | Box Q11 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
#DIV/0! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Calculation of HLP allowing for measured heat recovery efficiency
|  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Enter the resulting CO2 emission per m² here: |  | Box Q12 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Fabric heat loss, box (35), W/K |  | (including thermal bridging)
CO2 saving expressed in kWh of electricity |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Adjusted air change rate (22) | #DIV/0!
Electricity saved by SFP |  | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Effective air change rate (25) | #VALUE!
|  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Heat loss coefficient (37) | #VALUE!
Energy saved (kWh/yr), to be entered in box (95) | Box Q13 | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | HLP (38), W/m²K | #VALUE!
Additional energy consumed (kWh/yr), to be entered in box (96) | Box Q14 | #VALUE! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Step 5 : Re-enter 0.00 into SAP calculator as the air permeability at 50 Pa |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Note: The above value of HLP is only for the purposes of assessing the HLP criterion for Code Level 6. A different value will be shown on the SAP worksheet but is corrected for at box (95).
#VALUE! |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
For box (95) and box (96) the fuel is electricity |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
The CO2 emissions from the SAP calculation now incorporate savings from the tested MVHR unit |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Important note If any of the SAP data input items are subsequently amended this spreadsheet must be used again to recalculate the data for boxes (95) and (96)
(*) Table Q2 & Q3 are found on the individual manufacturer's test data sheets Download these from the website database
Version 02 April 2008
Note on E26: Uses agreed +40% In use rating for rigid ductwork
Note on E27: Uses agreed +70% In use rating for flexible ductwork
Note on E32: Uses agreed -15% In use rating for insulated ductwork
Note on E33: Uses agreed -30% In use rating for uninsulated ductwork